## Summary Sheet
Total Cost in Rs | 0

## BOQ
BILL OF QUANTITES
Name of work:Proposed Renovation of Lecture Hall in Room No. 212 and creation of New Lecture Hall in Room No. 307 at Administrative Building, IDRBT Premises, Masab Tank, Hyderabad.
S. No. | Description | Unit | Quantity | Rate(Rs.) | Amount (Rs.)
CIVIL WORKS
1 | DISMANTALING WORKS
DISMANTILING, REMVOING AND CARTING AWAY OF EXISTING ITEMS
Dismantling, Removing and Carting way the following existing items as directed and carting away debris from the site to the contractor own dump yard. The work shall be carried out as per the directions of the Architect. The rate shall be inclusive of all the labour, transportation necessary required for the complete execution of the item as directed by the architect / IDRBT. The site to be cleaned.
1.a | Removal of existing flooring tiles . All floor to be levelled to receive new stepped flooring as per design.
1.b | Existing Brick work to be demolished to mark new door openings
1.c | Dismantling of existing brickwork/ partition separating the Program Office room and existing lecture hall 212 .
| COST OF DISMANTALING WORKS | LS | 1 | 0 | 0
2 | BUY-BACK ITEMS
A comprehensive quote for Buy back old items. The prospective bidders to inspect the site and equipment’s in person before providing a firm quote.
2. a | All loose furniture , blinds, soft boards, writing boards etc.
2.b | Existing False Ceiling Tiles and Grid and all electrical fixtures.
2.c | Old ductable Air conditioning systems, including the indoor units, the outdoor units, Grills, dampers etc. and all connecting copper refrigerant pipes along with necessary components in total. A Existing AC ducting, diffuser grills and Indoor AHU along with all ancillary works.
2.d | Existing Doors as noted on the drawing, along with frame and hardware.
2.e | Existing windows to be removed. Opening to be re-plastered and finished to receive new windows as specified
| COST OF BUY-BACK ITEMS (-) | LS | 1 | 0 | 0
3 | BRICK WORK
3.a | 115 THK BRICK WORK FOR INTERNAL WALLS | Sq.M. | 25 | 0 | 0
Providing and constructing half-brick masonry partition walls in Superstructure using locally available approved quality Bricks, well (Kiln/Chimney) burnt, uniform size and colour having average crushing strength not less than 50 kg/cm2 . Rate includes providing RCC patli beam 100mm thick including providing with 4 nos. 8 mm dia TMT bars and 8 mm dia TMT links at 300 c/c in cement concrete of mix M 20 at mid-height (height between two patli not exceeding 1.20m), required formwork etc. in proper line, levels and plumb including raking out joints, curing, necessary scaffolding, etc. complete at any levels below plinth as per the approved drawing and as per instructions of Architect / Engineer. The rate shall be inclusive of all the material, labour, hardware, transportation necessary required for the complete execution of the item as directed by the Architect / Bank's Engineer. Using Cement Mortor 1:4. Rate should be quoted considering execution of work in the Second and Third floor level.
3.b | INTERNAL WALL PLASTERING | Sq.M | 200 | 0 | 0
Providing and applying in position average 16 mm thick smooth finish cement Plaster in cement mortar 1:5 to all internal walls, using fine or Coarse sand and adding polypropylene fiber of approved quality in desired quantity per bag of cement as per manufacturers specifications complete. Rate includes providing chicken mesh to all joints of RCC members with Brick walls in all positions in proper line, level & plumb at all levels and heights with necessary scaffolding, cleaning of surfaces, raking out joints, roughening of surfaces, curing etc. complete as directed at site. Rate includes making Flush/ raised/sunk or moulded bands of any width, recesses, making grooves etc. complete as per Architectural drawings and no extra payment shall be considered for the same as directed by the Architect / Bank's Engineer. The rate shall be inclusive making Flush/raised/sunk or moulded bands of any width, recesses, making grooves and all the material, labour, hardware, transportation necessary required for the complete execution of the item as directed by the Architect / Bank's Engineer. Approved make for Cement : ULTRATECH, ACC, RAMCO, INDIA,AMBUJA.
3.c. | INTERIOR WALL PAINTING | Sq.M. | 250 | 0 | 0
Providing, supplying and applying putty finish and finished to the walls of three coats and finished with one coat primer and three coats of Royal Emulsion paint to the walls of approved and shade to suit the interior of the class room. The rate shall be inclusive of all the necessary material required hardware, labour, transportation , necessary for the complete execution of the item as directed by the Architect /Institute.
3.d | LINTEL FOR NEW DOOR OPENINGS | Nos | 4 | 0 | 0
New door openings created to be spanned with new lintel. Plastered, painted and finished to match adjacent wall
3.e | SUB FLOOR WITH AAC BLOCKS | Cum | 400 | 0 | 0
New tiered sub floor raised with light weight AAC blocks. Plastered and leveled, ready to receive new SPC flooring. All rough flooring to be levelled with no undulations to receive new SPC Flooring as per manufacturer's instructions. Average measurments: 20m (L) x 10m (W) x 1m (H)
INTERIOR WORKS
1 | WALL PANELING
1.a | HDF Acoustic wall Panel
| Preparation of Surface: GI struts of Web Width 50mm, depth 25mm, 0.6mm thickness & 15mm symmetric flange are used to form CC – 600mm framing on both the planar sides (Vertical & Horizontal). Above this framing, Aluminum CC - 18 of Width 15mm, depth 18mm, 0.5mm thickness & 8mm symmetric flange are fixed Perpendicular Forming Center distance of 400mm. The slats are than fixed Perpendicular to CC-18 using Edge & Center Clips with a provision of joint expansion. STRICTLY FOLLOW MANUFACTURER'S INSTRUCTIONS for installation Provision for Concealed lighting to be given as noted in the drawings | Sq.m. | 224 | 0 | 0
1.b | Acoustic PET Panel
| 3D printed PET Panel for colour and highlighting – design and make as specified. Preparation of surface same as above. STRICTLY FOLLOW MANUFACTURER'S INSTRUCTIONS for installation. Provision for Concealed light and wall mount surface light to be given as noted in the drawings | Sq.M. | 19 | 0 | 0
1.c | Acoustic Slat Wall Panel
| Preparation of Surface: GI struts of Web Width 50mm, depth 25mm, 0.6mm thickness & 15mm symmetric flange are used to form CC – 600mm framing on both the planar sides (Vertical & Horizontal). Above this framing, Aluminum CC - 18 of Width 15mm, depth 18mm, 0.5mm thickness & 8mm symmetric flange are fixed Perpendicular Forming Center distance of 400mm. The slats are than fixed Perpendicular to CC-18 using Edge & Center Clips with a provision of joint expansion. STRICTLY FOLLOW MANUFACTURER'S INSTRUCTIONS for installation Provision for Concealed lighting to be given as noted in the drawings | Sq.M. | 70 | 0 | 0
1.d | Acoustic Fabric Panel
| Fabric Panel – design and make as specified. Preparation of surface same as above. Fabric samples to be approved by institue and Architect before installation. Provision for wall mount surface light to be given as noted in the drawings. | Sq.M. | 60 | 0 | 0
2 | FALSE CEILING
2.a | ACOUSTIC WOODEN PERFORATED PRELAMINATED BOARD – NISHABD by Mechtrix or equivalent – 2' x 2' HDHMR (water proof) boards | Sq.m. | 220 | 0 | 0
All suspended GI framing, channels, clips and clamps and installation as per Manufacturer's Instruction
2.b | Providing and fixing in position suspended gypsum false ceiling with G.I. suspension system and 12mm thk. Gypsum board of Saint-Gobain Gyprock / India Gypsum make duly finished with POP punning and 3 coats of plastic emulsion paint etc. Required cut- outs to be provided for specified light fixtures, AC diffusers and fire system complete. ( Refer to RCP drawings for design and fixture locations) | Sq.m. | 233 | 0 | 0
2.c | Providing & Fixing of 600X600 Armstrong Mineral Fibre Regular Suspended Ceiling System The suspension system used shall be Armstrong system and all installation procedures as per company recommended standard procedures. | Sq.m. | 19 | 0 | 0
3 | WALL /CEILING PAINT
ACRYLIC EMULSION PAINT
| Painting with two or more coats of acrylic emulsion paint of approved shade and colour of odor-free Nerolac Eco paint/Asian paints/Berger or equivalent make to partitions, walls, columns and any other exposed surface, applied evenly to give a approved uniform finish including preparation of the surface and primer coat etc. complete. | Sq.m. | 93 | 0 | 0
4 | FLOORING
4.a | SPEAKER'S PODIUM -SPC FLOOR
| 5mm thick SPC floor WELSPUN or Equivalent laid on leveled subfloor, Adhesive and laying instructions as per Manufacturer's instruction. Colour as specified in the drawings and finish schedule | Sq.m | 28 | 0 | 0
4.b | COMPLETE LECTURE HALL (except Podium)
| 5mm thick SPC floor WELSPUN or Equivalent laid on leveled subfloor, Adhesive and laying instructions as per Manufacturer's instruction. Colour as specified in the drawings and finish schedule. | Sq.m | 400 | 0 | 0
4.c | GRANITE SKIRTING – ALL VERTICAL RISER AND NOSING | Sq.m. | 47 | 0 | 0
Black granite skirting at all vertical risers, skirting and nosing as per detail. Edge of granite to be chamfered at the interface between SPC and granite for smooth transition. Refer to detail.
5 | WOOD WORK
5.a | CURVILINEAR TABLES (T-1 THRU T-15) | Sq.m. | 79 | 0 | 0
P/F Built in curvilinear tables made out of 19 mm thk BWP Grade Marine Ply 2' 6" high x 20" deep and finished in 1mm thick laminate as specified in drawing. Each table to be provided with POP-UP Electrical boxes for power and networking. Refer to Electrical / Interior detail drawings.
5.b | PODIUM / LECTERN (FX-1) | Sq.m. | 1.12 | 0 | 0
Podium -made of 19mm thk BWP Grade Marine ply finished in 1mm thick laminate as specified in drawing. Podium to be on 4-way castors to facilitate easy movement. Provision to be made for equipment under counter, Laptop display and Microphone
5.c | SERVER RACK (FX-2) | Sq.m. | 1.86 | 0 | 0
DB rack as per drawing made of 19 mm thk BWP Grade Marine Ply. Finished in specified 1mm Laminate
6 | DOORS
| Existing 5'-0” wide (opening size) double door to be reused. Inside face of Door (when Closed) to match the adjacent Slat Wall Panelling. Handle, Lock and Closure to be Concealed. The door shall be provided with approved make lock, heavy duty door closer,and concealed brass oxidized hinges, SS Brush finish handle of 12" on exterior side of approved design & fixing the same in position, etc. All S.S hardware to be 304 grade. | Nos | 4 | 0 | 0
7 | WINDOWS
| Provide and Fixing UPVC windows – Fenesta / Aparna Venstar or equivalent with Acoustic double panel glass and complete sound proof. All handles hardware and lock included | Sq.m. | 25 | 0 | 0
8 | BLINDS
| Providing and fixing of Sunscreen black out blinds with the fabric allowing no light passage through it. The fabric to have a PU Coating to control over light | Sq.m | 25 | 0 | 0
9 | GLASS WRITING BOARDS
| Providing and installation of 6mm thk back painted extra clear toughened glass of Saint Gobain make or equivalent over 12mm BWP ply secured firmly to aluminum/ply framing of partition or masonry wall. Glass to be mounted with required SS hardware hettich or Enox | Sq.m | 15 | 0 | 0
10 | GRANITE JAMS FOR WINDOWS
Providing & Fixing of in position 18 mm thick (+)/(-) 2mm machine cut . Telephone Balck Mirror polished Granite as per the approved sample for window cills, jams or any other specified etc. as per the drawing laid to the required level & line including cutting of stone to the required size & shape, edge polisheing / chamfered edges, surface preparation including cement backing with 1:1 cement grout, filling & finsihing the joints with cement & approved colour pigments, cutting, mirror polishing , curing , cleaning etc. The ratre shall be inclusive of all the material, labour , hardware, transport necessary required for the complete execution of the item as directed by the Architect / IDRBT (Basw cost of Granite Rs.1650 per sqmts ) (Base rate menas excluding GST, Transportation and Loading and Unloading charges)
| 300 MM Wide for 230 mm THK Walls for widnows & External doors | RM | 35 | 0 | 0
MEP WORKS
1 | Supply and laying of 25mm dia 2.0mm thick P.V.C.pipe ISI mark of Sudhakar / Maco Plast / Modi make concealed in wall with PVC junction boxes and all required accessories including masonary work for light, fan and separate plug point with supply and fixing of suitable size Metallic deep box including all labour charges etc. | mtr | 1000 | 0 | 0
2 | Supply and Fixing of 25mm dia 2.0mm(Heavy) thick Surface P.V.C.pipe ISI mark of Sudhakar / Maco Plast / Modi make with PVC junction boxes fixing on chromium plated metallic base saddles including all required materials and labour charges etc., complete for run of mains | mtr | 600 | 0 | 0
3 | Supply and Fixing of 32mm dia 2.5mm(Heavy) thick Surface P.V.C.pipe ISI Mark of Sudhakar / Maco Plast / Modi make with PVC junction boxes fixing on chromium plated metallic base saddles including all required materials and labour charges etc. | mtr | 100 | 0 | 0
4 | Wiring with 2 runs of 21/0.3mm (1.5 Sq.mm) FRLS PVC insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe with Supply and fixing of 6A/10A 1way Modular switch, ceiling rose and suitable cover frame of ISI Mark GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes including fixing, giving connections and all labour charges etc., complete for light and bell points. | pt | 8 | 0 | 0
5 | Wiring with 2 runs of21/0.3mm (1.5 Sq.mm) FRLS PVC insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe with Supply and fixing of 6A/10A 1way Modular switch, ceiling rose and suitable cover frame of ISI Mark GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes including fixing, giving connections and all labour charges etc., complete for TWO light points. | Pt | 70 | 0 | 0
6 | Supply and fixing of 6A 3/2 pin Modular socket with Switch and cover frame of Mossaic / L&T / North West / MK / Salzer make on a common switch board with earth connections and all labour charges etc., complete. | Each | 8 | 0 | 0
7 | Supply and fixing of 6A Modular Switch, 3/2 pin sockets, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc.(Raw power sockets) | Each | 8 | 0 | 0
8 | Supply and fixing of No.s 6A Modular Switches, 2 No.s 3/2 pin sockets, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc.(Raw power & UPS sockets) | Each | 4 | 0 | 0
9 | Supply and fixing of 16A Modular Switch,5 pin socket, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc.(Raw power sockets) | Each | 4 | 0 | 0
10 | Supply and fixing of 6A Modular Switch,3 No.s 3/2 pin sockets, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc.(UPS sockets) | Each | 40 | 0 | 0
11 | Supply and fixing of 6A Modular Switch,3 No.s 3/2 pin sockets, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc.(Raw power sockets) | Each | 4 | 0 | 0
12 | Supply and fixing of 6A Modular Switch, 3/2 pin sockets, suitable Modular box with cover frame of GM / Legrand Mossaic / L & T / North West / M K / Salzer / Indo Simon makes, including giving connections and all labour charges etc. (UPS sockets) | Each | 2 | 0 | 0
13 | Supply and fixing of Legrand / L & T / GE / Siemens / Schneider/ ABB. make DB with 1 No 20A single phase plug and Socket, in sheet steel enclosure with 1 No 10A to 20A 10 KA SP MCB including internal connection and labour charges for Flush Mounting etc. | Each | 2 | 0 | 0
14 | Supply and Run of 2 of 36/0.3mm (2.5 Sq.mm) FR / FRLS P.V.C. insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe for run of mains inlcuding all labour charges etc. | mtr | 2400 | 0 | 0
15 | Supply and Run of 2 of 56/0.3mm (4.0 Sq.mm) FR / FRLS P.V.C. insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe for run of mains inlcuding all labour charges etc. | mtr | 400 | 0 | 0
16 | Supply and Run of 1 of 14/0.3mm (1.0 Sq.mm) FR / FRLS P.V.C. insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe for earth continuity inlcuding all labour charges etc. | mtr | 1000 | 0 | 0
17 | Supply and Run of 1 of 36/0.3mm (2.5 Sq.mm) FR / FRLS P.V.C. insulated flexible ISI mark copper cable of Finolex / RR kabel / Fortune Art EBXL. make in existing pipe for earth continuity inlcuding all labour charges etc. | mtr | 500 | 0 | 0
18 | Supplying, testing and commissioning of 6 Sqmm 4 Core XLPE insulated,1100V grade armoured copper cable as per specification confirming to IS 7098(part-I). Makes: Finolex/ Torrent /Universal/ Polycab/Havells/unicab. | mtr | 300 | 0 | 0
19 | Supplying, testing and commissioning of 10 Sqmm 4 Core XLPE insulated,1100V grade armoured alluminium cable as per specification confirming to IS 7098(part-I). Makes: Finolex/ Torrent /Universal/ Polycab/Havells/unicab. | mtr | 200 | 0 | 0
CABLE GLANDS
20 | Supplying, testing and commissioning of Single compression brass cable glands for 4 Core XLPE armoured cable upto 16 Sqmm with brass washers complete. | each | 20 | 0 | 0
CABLE LUGS
21 | Supplying, testing and commissioning of copper Lugs confirming to IS specifications for cable upto 16 Sqmm including nuts and bolts with connections | each | 80 | 0 | 0
22 | Supply of Electronic Regulator of Modular of GM / Legrand Myrius / L & T / North West / M K / Salzer / Indo Simon / ABB /Schneider ZEN celo. | each | 2 | 0 | 0
23 | Supply, Transportation and Fixing of 12"(300mm) 250V 900 RPM Heavy duty ISI mark of Crompton / Bajaj / Havells / Orint Make exhaust / Fresh Air fan with metallic body and blades including making hole in wall and masonary work and all labour charges etc. | Each | 2 | 0 | 0
24 | Supply and fixing of 4 way TPN DB with IP-43 Protection with 1 No 40A FP RCCB 100mA and 12 Nos 6-32 A 10kA SP MCBs of Legrand / L & T / GE / Siemens / Schneider/ ABB. make including internal connections and labour charges for Flush Mounting etc. | Each | 4 | 0 | 0
25 | Supply and fixing of 8way VTPN DB with IP-43 Protection with 1 No 125 A FP MCCB and 8 Nos 63 A TP MCBs of Legrand / L & T / GE / Siemens / Schneider/ ABB. make including internal connections and labour charges for Flush Mounting etc. | Each | 2 | 0 | 0
26 | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc. | Mtr | 200 | 0 | 0
27 | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc. | Mtr | 500 | 0 | 0
LAN / TEL CONDUIT
28 | Supply and Laying of 25mm dia 2.0mm thick PVC pipe ISI mark of Sudhakar / Maco Plast / Modi make concealed in Roof Slabs / Floor with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc. | mtr | 400 | 0 | 0
29 | Supply and Fixing of 25mm dia 2mm(Heavy) thick S concealed ISI mark of Sudhakar / Maco Plast / Modi make with PVC / Metallic junction boxes fixing on wall with chromium plated metallic base saddles including all required materials and labour charges etc. | mtr | 100 | 0 | 0
30 | Supply and laying of LAN Cable cat - 6 (A) UTP cable of makes D Link / KMP / Molex. | Mtr | 2400 | 0 | 0
31 | Supply and fixing of CAT-6 RJ-45 information outlets including single base plate Makes: D link/ AMP / Molex / Legrand / Krone | Each | 10 | 0 | 0
32 | Supply, Transportation & fixing of 18W/20W 1700lumins,1200mm length , T5 LED Tube light fitting with extruded alluminium housing ,input voltage AC 165-260 Volts with > 0.9 PF with driver and frosped cover etc.,complete with 3 years warranty. Make:Philips / Osram / GE /Crompton / VIN / Bajaj / Havells / Halonix | Each | 4 | 0 | 0
33 | Supply and fixing of LED wall bracket Light point.complete | Each | 10 | 0 | 0
34 | Supply & Transportation & fixing of 18W LED down lighter Ressed / Surface mounting made of diecast alluminium body with powder coating,acrilic diffuser with Driver,operating voltage range of 150-265V AC,Power factor >0.9 high power 6 Nos of 1W LED 1W having efficacy of > 120 lumens /watt etc.,complete with 3 years warranty. Philips/GE / Crompton/VIN/ Bajaj/Havells make including cost & conveyance & labour charges. | Each | 106 | 0 | 0
35 | Supply & Transportation & fixing of 22W LED 2'x2'Ressed / Surface mounting made of diecast alluminium body with powder coating,acrilic diffuser with Driver,operating voltage range of 150-265V AC,Power factor >0.9 high power LED having efficacy of > 120 lumens /watt etc.,complete with 3 years warranty. Philips/GE / Crompton/VIN/ Bajaj/Havells make including cost & conveyance & labour charges. | Each | 14 | 0 | 0
36 | Supply and installation testing and commissioning of of LED Strip lighting | Mtr | 20 | 0 | 0
VRF HIGH SIDE
37 | Supply, Testing and Commissioning of Variable Refrigerant Flow (VRF / VRV) Outdoor condensing unit comprising of Invertor SCROLL compressor's, Heat Exchanger, propeller / axial fans, refrigerant Circuit, Safety Devices & Oil Recovery System, operating on R410a refrigerant gas. Necessary Refrigerant Gas and oil charge as per the deisgn.Compressor shall be equipped with inverter controller of Insulated Gate Bipolar Transistor (IGBT) type to be efficient & quiet. The outdoor unit shall have the multi-step of capacity control to meet load fluctuation and indoor unit individual control. Heat Exchanger shall be constructed with copper tubes mechanically bonded to aluminium fins to form a cross fin coil. Aluminium fins shall be covered by anti- corrosion resin film. Refrigerant Circuit shall include an accumulator, liquid and gas shutoff valves and a solenoid valves. The Outdoor unit shall include the following safety devices : High pressure switch, Low pressure switch, Fan motor safety thermostat, Inverter overload protector, Over Current relay, Fusible plugs, Fuses etc . Unit shall be equipped with an oil recovery system to ensure stable operation with long refrigerant piping. The unit shall be prewired in factory for necessary power and control wiring. All outdoors units shall be mounted with necessary vibration isolators ,Complete clamping and saddling of cabling work and refrigerant piping as per the specifications and approved drawings.
Nominal Cooling Capacity at ARI conditions
a | 8 HP OUT DOOR UNIT | Nos | 4 | 0 | 0
38 | 4 WAY CASSETTE UNITS:
Supply of4 WAY CASSETTE Type indoor unit. The housing of the unit shall be powder coated galvanised steel and shall include prefilter, fan section, coil section , fan section with low noise fan with Multi speed motor ,condensate drain pump , Insulation, pipe connections , all necessary controls, valves and fittings, strainer, drier , Fresh air intake and Painting as per the client requirement. The fan shall be with Aerodynamically designed diffuser turbo fan type. The cooling coil shall be of seamless copper tubes and shall have aluminium fins. Unit shall have filter cleanable type of resin net fixed to an integrally molded plastic frame. Unit shall have one way supply air grilles on sides and return air grill in center. Unit shall have high lift drain pump, fresh air intake provision, low gas level detection system. Unit shall have an electronic expansion valve which control refrigerant flow rate in respond to load variations of room. Unit to be provided with microprocessor with Wirless Remote controller thermostat as per the specifications and approved drawings.
a | 2.0 TR | Nos | 2 | 0 | 0
a | 4.0 TR | Nos | 8 | 0 | 0
VRF LOW SIDE
INSTALLATION OF VRV/VRF UNITS:
39 | OUTDOOR CONDENSING UNIT:
a | 8 HP OUT DOOR UNIT | Nos | 4 | 0 | 0
40 | 4- WAY CASSETTE UNITS:
a | 2.0 TR | Nos | 2 | 0 | 0
b | 4 TR | Nos | 8 | 0 | 0
41 | REFRIGERANT PIPING:
a | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 18swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type 'K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . and Insulation covered with 7 mil thick chemically treated woven glass cloth having density 205+/- 10 g/sqm and affixed using synthetic contact adhesive of approved make and protective coating of starbond 30-36 for Inside / Exposed Piping as per the specifications and approved drawings.
i | Ø 41.28 mm | Rmt | 30 | 0 | 0
ii | Ø 34.9 mm | Rmt | 40 | 0 | 0
iii | Ø 28.5 mm | Rmt | 80 | 0 | 0
iv | Ø 22.2 mm | Rmt | 60 | 0 | 0
v | Ø 19.1 mm | Rmt | 100 | 0 | 0
vi | Ø 15.9 mm | Rmt | 152 | 0 | 0
vii | Ø 12.7 mm | Rmt | 40 | 0 | 0
viii | Ø 9.52 mm | Rmt | 80 | 0 | 0
ix | Ø 6.53 mm | Rmt | 40 | 0 | 0
42 | DRAIN PIPE:
a | Supply, Installation, Testing and Commissioning of CPVC (Chlorinated Poly Vinyl Chloride) pipes condensate drain piping insulated using 9 mm thick nitrile rubber tubes including fitting and supports as per the specifications and approved drawings.
i | Ø 25 mm | Rmt | 100 | 0 | 0
ii | Ø 32 mm | Rmt | 40 | 0 | 0
43 | ELECTRICAL WORKS & CONTROL WIRING:
a | Supply, Installation, Testing and Commissioning of POWER CABLING of Copper cable for indoor / outdoor units to be suitably laid in PVC conduit as per site requirement.
i | 3C x 2.5 sq.mm. (Copper) (From MCB near unit to each IDU). | Rmt | 280 | 0 | 0
ii | 4C x 10 sq.mm. (Copper) (From Main Panel near unit to Outdoor Unit). | Rmt | 100 | 0 | 0
b | Supply, Installation, Testing and Commissioning of CONTROL CABLING of 3C x 1.5 sq.mm. copper cable for communication between indoor and outdoor units to be suitably laid in PVC conduit as per site requirement. | Rmt | 400 | 0 | 0
c | Supply, Installation, Testing and Commissioning of REMOTE CABLING of 4C x 1 Sq.mm. copper cable between each IDU & its wired remote to be suitably laid in PVC conduit as per site requirement. | Rmt | 224 | 0 | 0
1 | MS supports/Platform
a | Supply and Installation of MS supports/Platform (Channels/Angles) with painting and all necessary accessories , as per per the approved drawing. | Per Unit | 4 | 0 | 0
a | Removing and re-Installation of 10TR indoor ductable unit with extension of copper piping up to 15feet and removing and rejoining of existing ducting with all necessary items to restore original operating conditions etc, complete | Per Unit | 1 | 0 | 0
PUBLIC ADDRESS SYSTEM
44 | Supply erection testing and commissioning of 6 Watt ceiling mounted speaker | Nos | 20 | 0 | 0
45 | Supply erection testing and commissioning of 480 Watts Mixing Amplifier | No | 2 | 0 | 0
46 | Supply erection testing and commissioning of Gooseneck Microphone | No. | 2 | 0 | 0
47 | Supply erection testing and commissioning of wire less microphone suitable fixing ceiling | No. | 8 | 0 | 0
48 | Supply and surface laying of 2 core-twin twisted 0.75sq.mm copper flexible cable in PVC Conduits | Mtrs | 500 | 0 | 0
| Total Amount in Rs (Excluding GST) |  |  |  | 0